## TECHNICAL SPECIFICATION SHEET
TECHNICAL SPECIFICATION
Customer : |  | M/s. COMPANY NAME
Project No : |  | WTT-BAN-0001
Project Description : |  | ZLD based Sewage Treatment Plant
Plant Capacity : |  | 150 M3/DAY
Revision : |  | 00
Date : |  | 2026-01-01
S.NO | DESCRIPTION | QTY | GENERAL CHARACTERISTICS | kW | VENDOR LIST | COUNTRY OF ORIGIN
DURING PHASE - 1
1 | ROTARY BRUSH SCREENER | 1 | 600 mm CHANNEL WIDTH, AUTOMATIC TYPE, SS316 | 0.37 | WTT INTERNATIONAL | INDIA
2 | LIFTING PUMP | 1W + 1S | 9.375 m3/h @ 1 BAR | 0.9 | GRUNDFOS / XYLEM / EBARA | DENMARK / ITALY / JAPAN
3 | LEVEL FLOAT | 2 | -- | -- | FAES | ITALY
4 | OIL SCRAPER SYSTEM | 1 | NON-METALLIC OIL SCRAPER MECHANISM, RCC TANK | 0.37 | WTT INTERNATIONAL | INDIA
5 | SLUDGE PUMP | 1W + 1S | 0.625 m3/h @ 1.5 BAR | 1.1 | EBARA / LOWARA | JAPAN / ITALY
6 | EQUALIZATION & NEUTRALIZATION SYSTEM | 1 LOT | SS316L DIFFUSER GRID PIPING | -- | WTT INTERNATIONAL | INDIA
7 | NEUTRALIZATION DOSING PUMP | 1W + 1SS | AUTOMATIC TYPE, MOC - TEFLON | 0.18 | PROMINENT / MILTON ROY | GERMANY) / USA
8 | BIOLOGICAL FEED PUMP | 1W + 1S | 6.25 m3/h @ 1 BAR | 0.9 | GRUNDFOS / XYLEM / EBARA | DENMARK / ITALY / JAPAN
9 | LEVEL MEASUREMENT | 1 | RADAR TYPE LEVEL TRANSMITTER |  | E+H / PUNE TECTROL | GERMANY / INDIA
10 | pH SENSOR | 1 | POTENTIOMETRIC - DIGITAL OUTPUT (4-20 mA) |  | E+H / HACH / PROMINENT | GERMANY / USA / GERMANY
11 | FLOW MEASUREMENT | 1 | ELECTRO MAGNETIC TYPE |  | E+H / SIEMENS | GERMANY
13 | DE-NITRIFICATION PUMP | 1W + 1S | 12.5 m3/h @ 1 BAR | 1.1 | GRUNDFOS / XYLEM / EBARA | DENMARK / ITALY / JAPAN
15 | BIOLOGICAL OXIDATION SYSTEM | 1 LOT | SS316L / PP-GF DIFFUSER GRID PIPING | -- | WTT INTERNATIONAL | INDIA
17 | BLOWER EQUALIZATION & BIOLOGICAL TANK AERATION | 1W + 1S | 212 m3/h @ 0.85 BAR, TRILOBE TYPE, VFD CONTROLLED FOR WORKING BLOWER | 7.5 | ROBUSCHI / AERZEN / ATLAS COPCO | ITALY / SWEDEN
18 | DO SENSOR FOR BIOLOGICAL TANK | 1 | 0-5 ppm RANGE | -- | E+H / HACH / PROMINENT | GERMANY / USA / GERMANY
19 | LAMELLA SETTLER | 1 | FRAME MOC - SS316, PACKS MOC - PVC | -- | WTT INTERNATIONAL | INDIA
21 | SLUDGE RECIRCULATION PUMP | 1W + 1S | 6.25 m3/h @ 0.6 BAR | 0.9 | GRUNDFOS / XYLEM / EBARA | DENMARK / CHINA / ITALY / JAPAN
22 | SLUDGE THICKENER | 1 | RCC TANK WITH ONLY PIPING, PIPING MOC - SS316L | -- | WTT INTERNATIONAL | INDIA
23 | SCREW PRESS | 1 | 0.5 m3/hr | 1.5 | WTT INTERNATIONAL | INDIA
24 | SCREW PRESS FEED PUMP | 1W + 1S | 0.5 m3/h @ 2 BAR, TYPE - AODD, MOC - PP | -- | INGERSOLL RAND / SANDPIPER | USA
25 | POLY PREPARATION UNIT | 1 | POLY PREPARATION TANK WITH ITS AGITATOR | 0.55 | WTT INTERNATIONAL | INDIA
26 | POLY DOSING PUMP FOR SCREW PRESS | 1W + 1SS | TYPE - SURFACE MOUNTED, MOC - CI | 0.37 | EBARA | JAPAN
27 | UV SYSTEM | 1 | UV LAMP - 2 NO QUARTZ SLEEVE - 2 NO WAVELENGTH - 253.7 nm SS316 – ELECTRO POLISHED UV REACTOR CHAMBER | -- | WTT INTERNATIONAL | INDIA
28 | UV FEED PUMP | 1 LOT | 7.5 m3/h @ 1.5 BAR | 1.1 | EBARA / LOWARA | JAPAN / ITALY
*The UV system proposed in Phase 1 will be utilized for disinfection of MBR permeate during Phase-2 & RO permeate during Phase-3.
ADDITIONAL SYSTEMS ADDED IN PHASE - 2
29 | SUBMERGED CERAMIC MBR SYSTEM | 1 LOT | TOTAL TRAIN - 1, PORE SIZE - 0.1 µ, MOC - CERAMIC | -- | WTT INTERNATIONAL | INDIA
30 | PERMEATE / BACKWASH PUMP | 1W + 1S | 16.7 m3/h @ 2 BAR, VFD CONTROLLED | 2.2 | EBARA / LOWARA | JAPAN / ITALY
31 | SLUDGE PUMP | 1W + 1S | 1.4 m3/h @ 1.5 BAR | 1.1 | EBARA / LOWARA | JAPAN / ITALY
32 | DOSING PUMP | 2W | AUTOMATIC TYPE, MOC - PP | 0.18 | PROMINENT / MILTON ROY | GERMANY / USA
33 | LEVEL MEASUREMENT | 1 | HYDROSTATIC TYPE LEVEL TRANSMITTER | -- | PUNE TECTROL | INDIA
34 | FLOW MEASUREMENT | 1 | ELECTRO MAGNETIC TYPE | -- | E+H / SIEMENS | GERMANY
35 | PRESSURE GAUGE | 1 | PERMEATE LINE | -- | FORBES MARSHALL | INDIA
36 | PRESSURE TRANSMITTER | 1 | PERMEATE LINE | -- | DANFOSS | GERMANY / DENMARK / INDIA
37 | TURBIDITY SENSOR | 1 | PERMEATE LINE | -- | E+H / HACH | GERMANY / USA
ADDITIONAL SYSTEMS ADDED IN PHASE - 3
38 | REVERSE OSMOSIS SYSTEM | 1 | TOTAL SKIDS - 1 SKID MOC - SS316 TOTAL ARRAYS - 2 |  | WTT INTERNATIONAL | INDIA
39 | RO FEED PUMP | 1W + 1S | 13.8 m3/h @ 4 BAR | 3 | EBARA / LOWARA | JAPAN / ITALY
40 | RO PRE FILTER | 1 LOT | TYPE - CARTRIDGE, HOUSING MOC - SS316 |  | WTT INTERNATIONAL | INDIA
41 | RO DOSING PUMPS | 3W + 1SS | AUTOMATIC TYPE, MOC - PP | 0.18 | PROMINENT / MILTON ROY | GERMANY / USA
42 | DOSING TANKS | 2 | LDPE | -- | WTT INTERNATIONAL | INDIA
43 | RO HIGH PRESSURE PUMP | 1W | 13.8 m3/h @ 10.4 BAR, VFD CONTROLLED | 11 | GRUNDFOS / LOWARA | DENMARK / ITALY
44 | PRESSURE VESSEL | 3 | NOMINAL DIMENSION - 8 INCH MOC - FRP |  | CODELINE / ROPV | INDIA / CHINA
45 | RO MEMBRANE | 18 | TYPE - SPIRAL WOUND MOC - COMPOSITE POLYAMIDE |  | HYDRANAUTICS / DUPONT | JAPAN / USA
46 | LEVEL MEASUREMENT | 2 | RADAR TYPE LEVEL TRANSMITTER |  | E+H / PUNE TECTROL | GERMANY / INDIA
47 | LEVEL FLOAT | 2 | - |  | FAES | ITALY
48 | FLOW MEASUREMENT | 2 | ELECTRO MAGNETIC TYPE (RO FEED, COMMON PERMEATE LINE) |  | E+H / SIEMENS | GERMANY
49 | FLOW MEASUREMENT | 3 | ROTAMETER INDIVIDUAL PERMEATE LINE) |  | DFLOW | INDIA
50 | pH SENSOR | 1 | POTENTIOMETRIC - DIGITAL OUTPUT (4-20 mA) |  | E+H / HACH / PROMINENT | GERMANY / USA / GERMANY
51 | PRESSURE INDICATOR | 5 | PRE-FILTER INLET & OUTLET, ARRAY-1 INLET, EACH ARRAY OUTLET |  | FORBES MARSHALL | INDIA
52 | PRESSURE TRANSMITTER | 5 | PRE-FILTER INLET & OUTLET, ARRAY-1 INLET, EACH ARRAY OUTLET |  | DANFOSS | GERMANY / DENMARK / INDIA
53 | CIP SYSTEM | 1 | SKID MOC - SS316 CIP AUTOMATION - PROVIDED |  | WTT INTERNATIONAL | INDIA
54 | CIP PUMP | 1W | 18 m3/h @ 3.5 BAR | 5.5 | EBARA / LOWARA | JAPAN / ITALY
55 | CIP PRE FILTER | 1 LOT | TYPE - BAG, HOUSING MOC - SS316 |  | WTT INTERNATIONAL | INDIA
56 | FLOW MEASUREMENT | 1 | ELECTRO MAGNETIC TYPE |  | E+H / SIEMENS | GERMANY
57 | pH SENSOR | 1 | POTENTIOMETRIC - DIGITAL OUTPUT (4-20 mA) |  | E+H / HACH / PROMINENT | GERMANY / USA / GERMANY
58 | PRESSURE INDICATOR | 2 | CIP PRE-FILTER INLET & OUTLET |  | FORBES MARSHALL | INDIA
59 | PRESSURE TRANSMITTER | 1 | CIP PRE-FILTER OUTLET |  | DANFOSS | GERMANY / DENMARK / INDIA
60 | CIP DOSING PUMP | 2W | MOC - PP | 0.18 | PROMINENT / MILTON ROY | GERMANY / USA
61 | PC BASED AUTOMATION | -- | -- | -- | WTT INTERNATIONAL | INDIA
62 | LIVE DATA MONITORING | -- | -- | -- | WTT INTERNATIONAL | INDIA